## Disclaimer
© 2011 ASHRAE
DISCLAIMER
By using this spreadsheet, the user acknowledges and agrees to the following terms:
The resources supplied here are for personal and office use by purchasers of Procedures for Commercial Building Energy Audits, Second Edition. These resources are provided “as is” without warranty of any kind, either expressed or implied. The entire risk as to the quality and performance of the resources is with the user. In no event will ASHRAE be liable to the user for any damages, including without limitation any lost profits, lost savings, or other incidental or consequential damages arising out of the use of or inability to use these resources.

## kBTU Conversions
Procedures for Commercial Building Energy Audits, Second Edition
Energy Units—kBtu Conversions
Multiply the baseline quantity by the conversion multiplier to obtain a result in kBtu.
| Fuel | Measured Units | Conversion Multiplier | Source
| Any | MMBtu | 1000
|  | therms | 100
|  | dekatherms | 1000
| Electricity | kWh | 3.4121
|  | MWh | 3412.142
| Natural Gas | ft^3 | 1.027
|  | CCF (100 x ft^3) | 102.7 | 2
|  | MCF (1000 x ft^3) | 1027 | 2
|  | therm | 100 | 2
|  | m^3 | 36.4
|  | MJ | 0.94782
|  | GJ | 947.8171
| Purchased Steam | 1000 Btu | 1
|  | 1000 lb (approx) | 970
|  | lb (steam, 15 psig, evap) | 0.94568 | 3
|  | lb (steam, 50 psig, evap) | 0.91206 | 3
|  | therm | 100
| Purchased Hot Water | 1000 Btu | 1
| Purchased Chilled Water | 1000 Btu | 1
|  | ton-hour | 12
| Oil #1 | U.S. gallon | 137.4 | 1
| Oil #2 | U.S. gallon | 139.6 | 1
|  | Imperial gallon | 167
|  | litre | 36.7
| Oil #3 | U.S. gallon | 141.8 | 1
| Oil #4 | U.S. gallon | 145.1 | 1
| Oil #5 | U.S. gallon | 148.8 | 1
| Oil #6 | U.S. gallon | 152.4 | 1
|  | Imperial gallon | 185
|  | litre | 40.7
| Diesel | U.S. gallon | 139 | 5
| Gasoline | U.S. gallon | 124 | 6
| Propane | U.S. gallon | 91.33 | 2
|  | cubic feet | 2.55 | 2
|  | Imperial gallon | 110
|  | litre | 24.2
| Anthracite Coal | ton | 25400
|  | short ton (coal) | 19953 | 4
Sources
1 | 2009 ASHRAE Handbook—Fundamentals, Table 6, page 28.7
2 | 2009 ASHRAE Handbook—Fundamentals, page 28.5
3 | 2009 ASHRAE Handbook—Fundamentals, Refrigerant-718 (steam) table, page 30.37
(note this is heat of vaporization only)
4 | ASTM Standard D388
5 | ASTM Standard D975
6 | ASTM Standard D4814
© 2011 ASHRAE

## Formulas and Properties
Procedures for Commercial Building Energy Audits, Second Edition
Formulas and Properties
| Formulas |  | Notes
| Sensible Air Conditioning | Btu/h = 1.08 * ΔT * cfm
| Latent Air Conditioning | Btu/h = 4.5 * cfm * ΔH
| Water Heating/Cooling | Btu/h = 500 * gpm * ΔT
|  | Btu/h = gpm * ΔT * 8.34 Btu/gal-ΔT * 60 min/h * 1 kW/1000 | Derivation
tons = gpm * ΔT/24
| Water hp | = ft head * gpm/3960
| Pump Motor hp | = water hp/(pump eff * motor eff)
| Pump Hydraulic hp | = gpm * (ft H2O)/3960
| Fan Motor hp | = cfm * SP/(6354 * Motor Eff * Fan Eff) | 6354 cfm * in. H2O/hp
| kW | = 0.746 * hp * (Load Factor)/(Motor Eff)
| EER | = (Btu/h of Cooling Delivered)/(W Input)
= (kBtu of Cooling Delivered)/(kWh Input)
| HSPF | = (kBtu of Heating Delivered)/(kWh Input) | Seasonal Avg
| COP | = EER/3.412
= 3.516/(kW/ton)
= 1/EIR
| kW/ton | = 12/EER
| EIR | = 1/COP
= (kW/ton)/3.516
Other Misc Unit Equivalents
| 1 hp | 0.7457 kW
| 1 ton | 12,000 Btu/h
| 1 lb H2O | 7000 gr
| 1 psi | 2.307 ft H2O
| 1 U.S. gallon | 0.1337 ft^3
| 1 Imperial gallon | 0.1605 ft^3
| 1 ft^3 H2O | 62.4 lbm H2O
| Material | Properties
| Steam | Enthalpy of Vaporization | 970 Btu/lb
| Water | Density | 8.34 lbm/gallon
|  | Specific Heat | 1 Btu/(lbm-°F)
| Propane | Heat of Combustion | 2500 Btu/ft^3
|  | Heat of Combustion | 21,560 Btu/lb
| Natural Gas | Heat of Combustion | 1000 Btu/ft^3
| Wood | Heat of Combustion | 8000 Btu/lb
|  | Density | 45 lb/ft^3
© 2011 ASHRAE