## Background
ASRAE 90.1 Kadj Calculation Tool
With the release of ASHRAE 90.1-1999 a procedure was added to allow for adjusting the minimum full load and part load efficiencies of water cooled centrifugals using a procedure call Kadj
This procedure was added for centrifugal chillers that often designed and optimized to operate at the job conditions and may not run at the standard AHRI 550/590 rating conditions
The procedure adjusts the minimum efficiency requirements based on the Kadj calculation factor which is a function of lift and chilled water conditions
It was first introduced in the ASHRAE 90.1-1999 standard using a tabular approach and tables are used to determine the revised COP. There is a calculation equation which approximates the tables, but is not exact and the controlling requirement is the table. Interpolation is required between the operating points, but extrapolation is not allowed.
The tabular approach was continued in the ASHRAE 90.1-2001 and ASHRAE-2004 Standard.
In the 2010 Standard the tabular approach was dropped and the controlling method was a calculation method which was based on Lift and chilled water temperature
It was revised some in each of the subsequent publications include ASHRAE 90.1-2013, and ASHRAE 90.1-2016
In the tab's in this spreadsheet you will find a calculation tool for each of the years for IP and SI which includes automatic lookup of the base minimum efficiency as well as checks on the limits for the equation
The use of each ASHRAE 90.1 Standard procedure will depend on what version of the ASHRAE 90.1 procedure has been adopted by the local efficiency regulations

## 90.1-2010 KADJ - IP
ASHRAE 90.1-2010 Standard
IP Units
Item | Value | Units/Options | Comment
Full Load Capacity | 600 | Tons | Full load rated capacity | A
Compliance Path | A | A or B | Selected compliance path as shown in table 6.8.1-3 | B
Reference cell | 0 |  | hidden field
Standard Full Load Efficiency | 0.57 | kW/ton | Standard Full Load Efficiency From ASHRAE 90.1 table 6.8.1 C for ASHRAE 2010 at standard rating conditions
Standard Part Load Efficiency IPLV) | 0.539 | kW/ton | Standard IPLV Efficiency From ASHRAE 90.1 table 6.8.1 C for ASHRAE 2010 at standard rating conditions
LvgEvap | 42 | ºF | Evaporator Leaving Water Temperature (Minimum of 36 F)
LvgCond | 91.16 | ºF | Condenser Leaving Water Temperature (Maximum of 115 F)
LIFT | 49.16 | ºF | CEWT-CLWT
LIFT Check | TRUE |  | hidden field
LIFT Check | OK | ºF | Insure that input values do not result in an Lift ≥20 or ≤80 ºF
A | 1.0228 | ─ | A=0.00000014592*(LIFT)^4-0.0000346496*(LIFT)^3+0.00314196*(LIFT)^2-0.147199*(LIFT)+3.9302
B | 0.997 | ─ | B=0.0015*LvgEvap+0.934
Kadj | 1.0197 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 0.55898 | kW/ton | full load efficiency / Kadj
Adjusted Part Load Efficiency (NPLV) | 0.52858 | kW/ton | part load efficiency / Kadj
Input Items
Calculation Outputs | do not change

## 90.1-2010 KADJ - SI
ASHRAE 90.1-2010 Standard
SI Units
Item | Value | Units/Options | Comment
Full Load Capacity | 2110 | kW | Full load rated capacity
Compliance Path | A | A or B | Selected compliance path as shown in table 6.8.1-3 | A
Reference cell | 0
Full Load Efficiency | 6.17 | COPR | Standard Full Load Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2010 at standard rating conditions | B
Part Load Efficiency (IPLV) | 6.525 | COPR | Standard IPLV Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2010 at standard rating conditions
LvgEvap | 7 | ºC | Evaporator Leaving Water Temperature (Minimum of 2.2 ºC)
LvgCond | 37 | ºC | Condenser Leaving Water Temperature (Maximum of 46.1 ºC)
LIFT | 30 | K | CEWT-CLWT
LIFT Check | TRUE
LIFT Check | OK | K | Insure that input values do not result in an Lift >=11.1 or <=44.4 K
A | 0.92817 | ─ | 0.0000015318*LIFT^4-0.000202076*LIFT^3+0.0101800*LIFT^2-0.264958*LIFT+3.930196
B | 1.0009 | ─ | B=0.0027*LvgEvap+0.982
Kadj | 0.929 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 5.7319 | COPR | full load efficiency * Kadj
Adjusted Part Load Efficiency (NPLV) | 6.0617 | COPR | part load efficiency * Kadj
Input Items |  |  | Note the example in the 2010 standard for SI has an error in the NPLV calculation
Calculation Outputs | do not change

## 90.1-2013 KADJ - IP
ASHRAE 90.1-2013 Standard
IP Units
Item | Value | Units/Options | Comment | A
Effective Date | After 1/1/2015 | before 1/1/2015 or after 1/1/2015 | New Efficiencies went into effect 1/1/2015 (actual date depends on local Building Standard) | B
Full Load Capacity | 600 | Tons | Full load rated capacity
Compliance Path | A | A or B | Selected compliance path as shown in table 6.8.1-3
Reference cell | 0 |  | hidden field
Standard Full Load Efficiency | 0.56 | kW/ton | Standard Full Load Efficiency From ASHRAE 90.1 table 6.8.1-3 for ASHRAE 2013 at standard rating conditions | Before 1/1/2015
Standard Part Load Efficiency IPLV) | 0.5 | kW/ton | Standard IPLV Efficiency From ASHRAE 90.1 table 6.8.1-3 for ASHRAE 2013 at standard rating conditions | After 1/1/2015
LvgEvap | 42 | ºF | Evaporator Leaving Water Temperature (Minimum of 36 F)
LvgCond | 91.16 | ºF | Condenser Leaving Water Temperature (Maximum of 115 F)
LIFT | 49.16 | ºF | CEWT-CLWT
LIFT Check | TRUE |  | hidden field
LIFT Check | OK | ºF | Insure that input values do not result in an Lift ≥20 or ≤80 ºF
A | 1.0228 | ─ | A=0.00000014592*(LIFT)^4-0.0000346496*(LIFT)^3+0.00314196*(LIFT)^2-0.147199*(LIFT)+3.9302
B | 0.997 | ─ | B=0.0015LvgEvap+0.934
Kadj | 1.0197 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 0.54918 | kW/ton | full load efficiency / Kadj
Adjusted Part Load Efficiency (NPLV) | 0.49034 | kW/ton | part load efficiency / Kadj
Input Items
Calculation Outputs | do not change

## 90.1-2013 KADJ - SI
ASHRAE 90.1-2013 Standard
SI Units
Item | Value | Units/Options | Comment |  | A
Effective Date | After 1/2015 | before 1/1/2015 or after 1/1/2015 | New Efficiencies went into effect 1/1/2015 (actual date depends on local Building Standard) |  | B
Full Load Capacity | 2110 | kW | Full load rated capacity
Compliance Path | A | A or B | Selected compliance path as shown in table 6.8.1-3
Reference cell | 0
Full Load Efficiency | 6.286 | COPR | Standard Full Load Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2013 at standard rating conditions
Part Load Efficiency (IPLV) | 7.041 | COPR | Standard IPLV Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2013 at standard rating conditions |  | Before 1/2015
LvgEvap | 6 | ºC | Evaporator Leaving Water Temperature (Minimum of 2.0 ºC) | 31 | After 1/2015
LvgCond | 37 | ºC | Condenser Leaving Water Temperature (Maximum of 46 ºC)
LIFT | 31 | K | CEWT-CLWT
LIFT Check | TRUE
LIFT Check | OK | ─ | Insure that input values do not result in an Lift >=11 or <=44
A | 0.89409 | ─ | 0.0000015318*LIFT^4-0.000202076*LIFT^3+0.0101800*LIFT^2-0.264958*LIFT+3.9302
B | 0.9982 | ─ | B=0.0027*LvgEvap+0.982
Kadj | 0.89248 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 5.6101 | COPR | full load efficiency * Kadj
Adjusted Part Load Efficiency (NPLV) | 6.2839 | COPR | part load efficiency * Kadj
Input Items |  |  | Note that the requirements and example in the published ASHRAE 2013 Standard is incorrect and was corrected by addendum CH so this tool is the correct calculation method
Calculation Outputs | do not change

## 90.1-2016 KADJ - IP
ASHRAE 90.1-2016 Standard
IP Units
Item | Value | Units/Options | Comment | A
Full Load Capacity | 600 | Tons | Full load rated capacity | B
Compliance Path | B | A or B | Selected compliance path as shown in table 6.8.1-3
Reference cell | 2 |  | hidden field
Standard Full Load Efficiency | 0.585 | kW/ton | Standard Full Load Efficiency From ASHRAE 90.1 table 6.8.1-3 for ASHRAE 2016 at standard rating conditions | Before 1/1/2015
Standard Part Load Efficiency IPLV.IP) | 0.38 | kW/ton | Standard IPLV Efficiency From ASHRAE 90.1 table 6.8.1-3 for ASHRAE 2016 at standard rating conditions | After 1/1/2015
LvgEvap | 42 | ºF | Evaporator Leaving Water Temperature (≥36 ºF and ≤ 60 ºF)
LvgCond | 91.16 | ºF | Condenser Leaving Water Temperature (≤115 ºF)
LIFT | 49.16 | ºF | CEWT-CLWT
LIFT Check | TRUE |  | hidden field
LIFT Check | OK | ºF | Insure that input values do not result in an Lift ≥20 or ≤80 ºF
A | 1.0233 |  | A=0.000000145920*(LIFT)^4-0.0000346496*(LIFT)^3+0.00314196*(LIFT)^2-0.147199*(LIFT)+3.93073
B | 0.997 | ─ | B=0.0015LvgEvap+0.934
Kadj | 1.0202 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 0.5734 | kW/ton | full load efficiency / Kadj
Adjusted Part Load Efficiency (NPLV.IP) | 0.37246 | kW/ton | part load efficiency / Kadj
Input Items
Calculation Outputs | do not change

## 90.1-2016 KADJ - SI
ASHRAE 90.1-2016 Standard
SI Units
Item | Value | Units/Options | Comment | A
Full Load Capacity | 2110 | kW | Full load rated capacity | B
Compliance Path | A | A or B | Selected compliance path as shown in table 6.8.1-3
Reference cell | 0
Full Load Efficiency | 6.286 | COPR | Standard Full Load Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2013 at standard rating conditions
Part Load Efficiency (IPLV) | 7.041 | COPR | Standard IPLV Efficiency From ASHRAE 90.1 SI table 6.8.1-3 for ASHRAE 2013 at standard rating conditions | Before 1/2015
LvgEvap | 6 | ºC | Evaporator Leaving Water Temperature (≥2.2 ºC and ≤ 15.6 ºC) | After 1/2015
LvgCond | 37 | ºC | Condenser Leaving Water Temperature (Maximum of 46 ºC)
LIFT | 31 | K | CEWT-CLWT
LIFT Check | TRUE
LIFT Check | OK | ─ | Insure that input values do not result in an Lift ≥11.00 K or ≤44.00 K
A | 0.89462 | ─ | 0.00000153181*LIFT^4-0.000202076*LIFT^3+0.0101800*LIFT^2-0.264958*LIFT+3.93073
B | 0.9982 | ─ | B=0.0027*LvgEvap+0.982
Kadj | 0.89301 | ─ | Off design condition adjustment for full load efficiency and IPLV
Adjusted Full Load Efficiency | 5.6135 | COPR | full load efficiency * Kadj
Adjusted Part Load Efficiency (NPLV.SI) | 6.2877 | COPR | part load efficiency * Kadj
Input Items
Calculation Outputs | do not change

## Efficiency 2007 (hidden)
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies IP
Path | A
Capacity | Full | Part
<Tons | COP | kW/ton
0 | 5 | 5.25
150 | 5.55 | 5.9
300 | 6.1 | 6.4
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies SI
Path | A
Capacity | Full | Part
kW | COP | COP
0 | 5 | 5.25
528 | 5.55 | 5.9
1055 | 6.1 | 6.4

## Efficiency 2010 (hidden)
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies IP
Path | A |  | B
Capacity | Full | Part | Full | Part
<Tons | kW/ton | kW/ton | kW/ton | kW/ton
0 | 0.634 | 0.596 | 0.639 | 0.45
150 | 0.634 | 0.596 | 0.639 | 0.45
300 | 0.576 | 0.549 | 0.6 | 0.4
600 | 0.57 | 0.539 | 0.59 | 0.4
Table 6.8.1c 2010 Centrifugal Minimum Efficiencies SI
Path | A |  | B
Capacity | Full | Part | Full | Part
kW | COP | COP | COP | COP
0 | 5.547 | 5.901 | 5.504 | 7.815
528 | 5.547 | 5.901 | 5.504 | 7.815
1055 | 6.106 | 6.406 | 5.856 | 8.792
2110 | 6.17 | 6.525 | 5.961 | 8.792

## Efficiency 2013 (hidden)
ASHRAE 90.1-2013 Table 6.8.1-3 IP |  |  |  |  | ASHRAE 90.1-2013 Table 6.8.1-3 SI
| Before 1/1/2015 |  |  |  |  | Before 1/1/2015
Path | A |  | B |  | Path | A |  | B
Capacity | Full | IPLV | Full | IPLV | Capacity | Full | Part | Full | Part
<Tons | kW/ton | kW/ton | kW/ton | kW/ton | kW | COP | COP | COP | COP
0 | 0.634 | 0.596 | 0.639 | 0.45 | 0 | 5.553 | 5.907 | 5.509 | 7.823
150 | 0.634 | 0.596 | 0.639 | 0.45 | 528 | 5.553 | 5.907 | 5.509 | 7.823
300 | 0.576 | 0.549 | 0.6 | 0.4 | 1055 | 6.112 | 6.412 | 5.867 | 8.801
400 | 0.576 | 0.549 | 0.6 | 0.4 | 1407 | 6.112 | 6.412 | 5.827 | 8.801
600 | 0.57 | 0.539 | 0.59 | 0.4 | 2110 | 6.176 | 6.531 | 5.967 | 8.801
| After 1/1/2015 |  |  |  |  | After 1/1/2015
Path | A |  | B |  | Path | A |  | B
Capacity | Full | IPLV | Full | IPLV | Capacity | Full | IPLV | Full | IPLV
<Tons | kW/ton | kW/ton | kW/ton | kW/ton | <Tons | COP | COP | COP | COP
0 | 0.61 | 0.55 | 0.695 | 0.44 | 0 | 5.771 | 6.401 | 5.065 | 8.001
150 | 0.61 | 0.55 | 0.635 | 0.4 | 528 | 5.771 | 6.401 | 5.544 | 8.801
300 | 0.56 | 0.52 | 0.595 | 0.39 | 1055 | 6.286 | 6.77 | 5.917 | 9.027
400 | 0.56 | 0.5 | 0.585 | 0.38 | 1407 | 6.286 | 7.041 | 6.018 | 9.264
600 | 0.56 | 0.5 | 0.585 | 0.38 | 2110 | 6.286 | 7.041 | 6.018 | 9.264

## Efficiency 2016 (hidden)
ASHRAE 90.1-2016 Table 6.8.1-3 IP |  |  |  |  | ASHRAE 90.1-2016 Table 6.8.1-3 SI
Path | A |  | B |  | Path | A |  | B
Capacity | Full | IPLV.IP | Full | IPLV.IP | Capacity | Full | IPLV.SI | Full | IPLV.SI
<Tons | kW/ton | kW/ton | kW/ton | kW/ton | <Tons | COP | COP | COP | COP
0 | 0.61 | 0.55 | 0.695 | 0.44 | 0 | 5.771 | 6.401 | 5.065 | 8.001
150 | 0.61 | 0.55 | 0.635 | 0.4 | 528 | 5.771 | 6.401 | 5.544 | 8.801
300 | 0.56 | 0.52 | 0.595 | 0.39 | 1055 | 6.286 | 6.77 | 5.917 | 9.027
400 | 0.56 | 0.5 | 0.585 | 0.38 | 1407 | 6.286 | 7.041 | 6.018 | 9.264
600 | 0.56 | 0.5 | 0.585 | 0.38 | 2110 | 6.286 | 7.041 | 6.018 | 9.264